## DEMCOPEM system tool
Hydrogen flow | 1000 | Nm3/h
Hydrogen pressure | 50 | mbarg
Power sizing criteria | Site power
Power requirement (net) | 1000 | kWel
Heat requirement (max 63°C) | 2000 | kWth
Utilities available
Cooling water | 15 | °C
Environment temperature | 25 | °C
Preliminary sizing |  |  | Plant performances |  | Energy balance
Total power production | 1020.1467 | kWel | Electric efficiency | 52.08% | El. power, site consumption | 1020.1467 | kW
Electric power export to grid | 0 | kWel | Thermal efficiency | 22.49% | El. power, exported to grid | 0 | kW
Heat production @ 60.0 °C | 440.6277 | kWth | PES | 29.98% | Recovered heat | 440.6277 | kW
Water production | 430.1538 | kg/h | Reference efficiency (PES) |  | Wasted heat | 351.8115 | kW
Actual hydrogen consumption | 658.5862 | Nm3/h | Separate electicity production | 44.2% | BOP consumption | 88.0177 | kW
Cooling power required | 59.4611 | kWth | Separate thermal production | 90% | DC/AC losses | 58.3244 | kW
Indicative plant footprint | 320 | m2 |  |  | H2 input | 1958.9281 | kW
WARNING: Energy balances are performed by means of simplified correlations for thermodynamic properties
The author(s) and members of the consortium cannot be held legally responsible for any mistake in printing or faulty instructions. The authors and consortium members retrieve the right not to be responsible for the topicality, correctness, completeness or quality of the information provided. Liability claims regarding damage caused by the use of any information provided, including any kind of information that is incomplete or incorrect, will therefore be rejected. The information contained on this website is based on author’s experience and on information received from the project partners.
Politecnico di Milano - Department of Energy - GECOS Group |  |  | www.gecos.polimi.it | www.demcopem-2mw.eu
0
0
0

## Calculator (hidden)
PEM fuel cell
Stacks data |  |  |  | Coefficients
Cells | 75 |  |  | A | 789.31 |  |  | H2 in max | 1000 | Nm3/h
Nominal current | 120 | A |  | B | 21.9 |  |  |  | 12.393 | mol/s
Nominal T | 65 | °C |  | C | 112.1
Nominal pressure | 1.3 | bar |  | D | -0.994 |  |  | Power req | 1050 | kWe | gross estimate
Nominal Sh | 1.25
Nominal So | 2 | [6 empty] | Nstacks | 266 | for H2
RHh | 80% |  |  | xH/xHref | 3.6298 |  |  |  | 171 | for EE
RHo | 80% |  |  | xO/xOref | 1.4592 |  |  |  | 171 | limiting | EE
Nominal voltage | 740.6278 | mV |  | xv | 0.19367 |  |  | Columns | 25 |  | Max | 7 | stacks per column
Nominal power | 6665.6504 | W | [5 empty] | Final | 175 | stacks
Actual current | 120 | A | [5 empty] | H2 in actual | 8.1619 | mol/s
Actual voltage | 740.6278 | mV | [6 empty] | 658.5862 | Nm3/h
Actual stack power | 6665.6504 | W
Gross power | 1166.4888 | kW
BOP
H2 compressor in | Δp | 0.15 | bar |  |  | Auxiliaries |  | 71.7465 | m2 |  |  |  | Cooling duties
| Pel | 16.7972 | kW |  |  | Stacks |  | 25.5208 | m2 |  |  |  | H2 compr | 32.9805 | kW
H2 compressor rec | Δp | 0.16 | bar | [9 empty] | H2 hum | 0 | kW
| Pel | 16.1833 | kW |  |  | Footprint |  | 320 | m2 |  |  |  | T control | 0 | kW
Air compressor | Δp | 0.15 | bar | [9 empty] | Cond | 26.4806 | kW
| Pel | 24.3467 | kW |  |  | Other aux | [7 empty] | 59.4611 | kW
Pumps | Pel, cool | 11.2033 | kW |  |  | Control system |  | 3 | kW
| Pel, hum | 6.4872 | kW |  |  | Conditioning |  | 10 | kW
BOP total | EE consumption | 88.0177 | kW
Inverter | η | 95%
Mass and energy balance
|  | Mass flow | T | p | h |  |  | Composition (molar) |  |  |  |  | xsat | kmol/s |  |  |  | MM | T | h[kJ/kmol]
| Description | kg/s | °C | barg | kJ/kg |  |  | hydrogen | water | nitrogen | oxygen |  |  | H2 | H2O | N2 | O2 | kg/kmol | K | H2 | H2O | N2 | O2
1 | Inlet H2 | 0.016454 | 25 | 0.05 | 3931.915 |  |  | 100% | 0% | 0% | 0% |  | 2.98% | 0.0081619 | 0 |  |  | 2.016 | 298.15 | 3931.915 | 104.8782 | 309.2665 | 271.0092
2 | Compr H2 | 0.016454 | 25 | 0.2 | 3931.915 |  |  | 100% | 0% | 0% | 0% |  | 2.612% | 0.0081619 | 0 |  |  | 2.016 | 298.15 | 3931.915 | 104.8782 | 309.2665 | 271.0092
3 | Mix H2 | 0.032116 | 25.9355 | 0.2 | 3718.5684 |  |  | 94.09% | 5.911% | 0% | 0% |  | 2.761% | 0.010202 | 0.00064097 |  |  | 2.9618 | 299.0855 | 3945.3546 | 108.7921 | 310.2409 | 271.873
4 | Hum H2 | 0.05342 | 63 | 0.2 | 3838.895 |  |  | 84.84% | 15.16% | 0% | 0% |  | 18.95% | 0.010202 | 0.0018235 |  |  | 4.4421 | 336.15 | 4477.861 | 263.8686 | 348.8496 | 306.1002
5 | Anode Exhaust | 0.015661 | 65 | 0.04 | 3494.4181 |  |  | 76.1% | 23.9% | 0% | 0% |  | 23.9% | 0.0020405 | 0.00064097 |  |  | 5.8406 | 338.15 | 4506.595 | 272.2366 | 350.9329 | 307.9471
6 | Compr Exh. | 0.015661 | 65 | 0.2 | 3494.4181 |  |  | 76.1% | 23.9% | 0% | 0% |  | 20.75% | 0.0020405 | 0.00064097 |  |  | 5.8406 | 338.15 | 4506.595 | 272.2366 | 350.9329 | 307.9471
7 | Air in | 1.1324 | 25 | 0 | 298.1619 |  |  | 0% | 1.564% | 77.76% | 20.67% |  | 3.128% |  | 0.00061743 | 0.030704 | 0.0081619 | 28.6806 | 298.15 | 3931.915 | 104.8782 | 309.2665 | 271.0092
8 | Compr air | 1.1324 | 40.4143 | 0.15 | 312.1155 |  |  | 0% | 3.247% | 76.43% | 20.32% |  | 6.494% |  | 0.00061743 | 0.030704 | 0.0081619 | 28.4982 | 313.5643 | 4153.3715 | 169.3708 | 325.3229 | 285.2435
9 | Hum air | 1.2338 | 63 | 0.15 | 327.8525 |  |  | 0% | 15.81% | 66.51% | 17.68% |  | 19.77% |  | 0.0062442 | 0.030704 | 0.0081619 | 27.1366 | 336.15 | 4477.861 | 263.8686 | 348.8496 | 306.1002
10 | Cathode exh | 1.1874 | 65 | 0.03 | 328.2928 |  |  | 0% | 23.89% | 67.18% | 8.929% |  | 23.89% |  | 0.01092 | 0.030704 | 0.0040809 | 25.9804 | 338.15 | 4506.595 | 272.2366 | 350.9329 | 307.9471
11 | Stack | 1.0178 | 30 | 0.01 | 302.2763 |  |  | 0% | 4.15% | 84.61% | 11.24% |  | 4.15% |  | 0.0015061 | 0.030704 | 0.0040809 | 28.0463 | 303.15 | 4003.75 | 125.798 | 314.4748 | 275.6264
12 | Cooling water | 45.419 | 63 | 0.01 | 263.8686 |  |  |  | 100% | [8 empty] | 18.016 | 336.15 |  | 263.8686
13 | Pump outlet | 45.419 | 63 | 2 | 263.8686 |  |  |  | 100% | [8 empty] | 18.016 | 336.15 |  | 263.8686
14 | Hum heater | 45.419 | 62.3176 | 1.528 | 261.0134 |  |  |  | 100% | [8 empty] | 18.016 | 335.4676 |  | 261.0134
15 | Heat recov out | 45.419 | 60 | 1.171 | 251.3168 |  |  |  | 100% | [8 empty] | 18.016 | 333.15 |  | 251.3168
16 | Water cell inlet | 45.419 | 60 | 0.81 | 251.3168 |  |  |  | 100% | [8 empty] | 18.016 | 333.15 |  | 251.3168
17 | Water cell outlet | 45.419 | 65 | 0.21 | 272.2366 |  |  |  | 100% | [8 empty] | 18.016 | 338.15 |  | 272.2366
[13 empty] | MM | 2.016 | 18.016 | 28.013 | 31.9988
[8 empty] | Qout | [6 empty] | F |  | h
Balances | Mix H2 in | IN | 119.4243 | OUT | 119.4243 | D39 | A | 0 | kW |  |  |  | Water out | Str 5 | 0.024245 | kg/s | 272.2366 | kJ/kg
| H2 hum | IN | 75.3289 | OUT | 205.0724 |  |  | -129.7435 | kW |  |  |  |  | Str10 | 0.059871 | kg/s | 272.2366 | kJ/kg
| PEM | IN | 13998.6413 | OUT | 13998.6413 | C49 | A | 0 | kW |  |  |  |  | Cond | 0.1696 | kg/s | 125.798 | kJ/kg
Mass check | 0.011543 | system | [10 empty] | Water in | Hum H2 | 0.032852 | kg/s | 104.8782 | kJ/kg
| -4.8971e-06 | cell | [11 empty] | Hum air | 0.10137 | kg/s | 104.8782 | kJ/kg
Pressure losses | Pipes H2 | 120 | mbar | HX | 472 | mbar | [7 empty] | Net | 0.11949 | kg/s
| Pipes air | 40 | mbar |  | 357 | mbar
| Cell anode | 40 | mbar |  | 361 | mbar
| Cell cathode | 100 | mbar
| Water circuit | 600 | mbar
𝑉=𝐴+𝐵𝑙𝑛(𝑥_𝐻 )+𝐶𝑙𝑛(𝑥_𝑂 )+𝐷𝐼